SITE-WIDE RADIOFREQUENCY RADIATION HAZARD (RFR) STUDY

Consolidated Earth Station Site — Call Sign E040269

2000 M Street NW, Washington, DC — 47 C.F.R. § 1.1307(b), § 1.1310 — IEEE Std C95.3-2021, Annex D

# 1. Scope

This study evaluates RF exposure compliance under 47 C.F.R. § 1.1310 for the consolidated earth station site at 2000 M Street NW, Washington, DC, covering all seven Ku-band transmit/receive antennas proposed under the modification of call sign E040269: the four existing E040269 antennas (2x Prodelin 3.8m, 2.4m Comtech, 5m RSI)  and the three antennas formerly authorized under expired call sign E890197 (5m Vertex, 5m Harris Microdyne, 2.4m Lucas), all operating 14.0–14.5 GHz uplink / 11.7–12.2 GHz downlink.

Near-field on-axis power density is computed using the relationship identified by the filer as IEEE Std C95.3-2021, Section D.4.4:  Snf = 16P / (η·π·D²), where P is transmit power (W), η is antenna aperture efficiency, and D is antenna diameter (m).

# 2. Antennas Evaluated and Aperture Efficiency

Transmit power (P) for each antenna was derived from its Schedule B Gain and EIRP: P (dBW) = EIRP (dBW) − Gain (dBi). Aperture efficiency (η) for the D.4.4 formula was derived from each antenna's own reported gain, diameter, and operating frequency (η = G / (πD/λ)²) rather than assumed generically, so the result is self-consistent with each antenna's actual Schedule B record. Derived efficiencies range from about 0.52 to 0.77, a physically reasonable range for commercial Ku-band reflector antennas.

# 3. Individual Antenna Results (On-Axis, Main Beam)

Far-field (Rayleigh) distance Rff = 2D²/λ. Beyond Rff, power density is taken to fall off as the inverse square of distance for purposes of estimating a compliance distance.

| Ant. ID | Source | D(m) | Gain(dBi) | EIRP(dBW) | η(derived) | P(W) | Rff(m) | Snf(mW/cm²) | R—Occ.5 mW/cm² (m) | R—Gen.1 mW/cm² (m) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 3.8M.PRO | E040269 | 3.8 | 53.2 | 76.3 | 0.650 | 204 | 1,372 | 11.08 | 2,042 | 4,567 |
| 2.4M.COM | E040269 | 2.4 | 48.2 | 74.3 | 0.515 | 407 | 547 | 69.93 | 2,046 | 4,576 |
| 4.6M.VER | E040269 | 4.6 | 54.5 | 76.67 | 0.598 | 165 | 2,010 | 6.63 | 2,315 | 5,177 |
| 3.8M.PRO2 | E040269 | 3.8 | 53.2 | 76.3 | 0.650 | 204 | 1,372 | 11.08 | 2,042 | 4,567 |
| A1 | E890197* | 2.4 | 49.2 | 73.2 | 0.648 | 251 | 547 | 34.25 | 1,432 | 3,202 |
| A2 | E890197* | 5.0 | 56.3 | 80.3 | 0.766 | 251 | 2,375 | 6.68 | 2,745 | 6,138 |
| A3 | E890197* | 5.0 | 55.0 | 79.3 | 0.568 | 269 | 2,375 | 9.65 | 3,300 | 7,379 |

# 4. Combined / Aggregate Exposure

Total simultaneous transmit power across all seven Ku-band antennas (worst case, all active at once): approximately 1,752 W.

Under the D.4.4 formula, the summed near-field on-axis power density across all seven antennas, if a location existed where every beam overlapped, is approximately 149.3 mW/cm². As with the individual results, this combined figure is a deliberately conservative, non-physical bound: it assumes all seven independently pointed rooftop antennas share a common boresight, which they do not in practice.  The antennas are spread across different corners of a rooftop.

# 5. Beam Geometry and Practical Hazard Zone

Each antenna's main beam is pointed at a fixed, elevated look angle toward its target geostationary satellite, not toward the ground or other rooftop equipment. The on-axis compliance distances in Section 3 remain a theoretical bound assuming continuous exposure directly on boresight, not a literal ground-level hazard radius for this site.

# 6. Mitigation and Access Control

- The rooftop is a restricted-access (occupational-controlled) area at all times — every antenna in Section 3 exceeds the occupational MPE within its own near field under this formula.

- RF hazard warning signage posted at each antenna and at all roof access points.

# 7. Conclusion

Using the D.4.4 near-field formula supplied by the filer, every Ku-band transmit antenna at this site exceeds both the occupational and general-population MPE limits within its near field. The site can be shown to comply with § 1.1310 for areas accessible to the general public, provided (a) the rooftop remains a restricted, occupational-controlled area, and (b) each antenna's elevation angle and site geometry are confirmed to keep the main beam away from occupied or publicly accessible space, per Section 5.

8. Certification

The undersigned certifies that this radiofrequency radiation hazard analysis was prepared in accordance with the cited standard(s) and reflects, to the best of the engineer's knowledge, the actual as-built configuration of the referenced earth station site.

Prepared by: _______________________________________          Date: ______________

Name / Title: ______________________________________